UNIcon MODBUS register description
 UNIcon softwareversion 10
The input register address range of 1000 – 1960 is divided into 64 blocks of 16 reigsters
z.B.:
register address 1000 to 1015 contains the values of ECblue info with address 1.
register address 1016 bis 1031 contains the values of ECblue info with address 2.
	Registerblock Adressoffset
	Wert
	ECblue Register Entsprechung

	0
	speed
	ECblue input register 14

	1
	Motorscurrent
	ECblue input register 15

	2
	Input power
	ECblue input register 33

	3
	Modulation
	ECblue input register 27

	4
	Error status
	ECblue input register 12

	5
	Operation condition
	ECblue input register 10

	6
	Product code
	ECblue input register 1

	7
	Firmware version
	ECblue input register 0

	8-15 
	Reserved for future use, reads 0
	

	
	
	

	
	
	


Tabelle 1
